## Candidate_Configurations
config_id | power_mw | energy_mwh | duration_hrs | chemistry | cooling_system | overnight_capex_usd | annualized_capex_usd | annual_fixed_om_usd | round_trip_efficiency | warranty_cycles
LFP-100-400 | 100 | 400 | 4 | LFP | Forced Air HVAC | 140000000 | 1680000 | 850000 | 0.86 | 3500
NMC-100-200 | 100 | 200 | 2 | NMC | Standard Air HVAC | 95000000 | 1140000 | 580000 | 0.92 | 2000
LFP-200-800 | 200 | 800 | 4 | LFP | Industrial Closed-Loop Liquid | 265000000 | 3180000 | 1473065 | 0.85 | 4000
VRFB-50-500 | 50 | 500 | 10 | Flow-VRFB | Electrolyte Chiller Loops | 210000000 | 2520000 | 1260000 | 0.72 | 10000

## Thermal_Derating_Curves
config_id | chemistry | threshold_temp_c | derate_pct_per_deg_above_threshold | max_operating_temp_c | auxiliary_cooling_load_pct | derate_notes
LFP-100-400 | LFP | 35 | 0.035 | 45 | 0.025 | Standard forced-air cooling derates above 35C ambient
NMC-100-200 | NMC | 35 | 0.07 | 42 | 0.04 | High thermal sensitivity; 35% capacity curtailment at 40C, accelerates degradation
LFP-200-800 | LFP | 38 | 0.015 | 48 | 0.018 | Industrial closed-loop liquid cooling maintains 94% firm capacity at 42C
VRFB-50-500 | Flow-VRFB | 40 | 0.02 | 45 | 0.055 | Auxiliary pumping load escalates rapidly above 35C; low power delivery

## Financial_Valuation_Model
parameter_key | parameter_description | unit | value | methodological_notes
voll_usd_per_mwh | Value of Lost Load for avoided unserved energy | USD/MWh | 12500 | Regulatory VOLL standard for critical unserved load
curtailment_arbitrage_usd_per_mwh | Value of absorbed renewable curtailment injected during stress/ramp | USD/MWh | 45 | Wholesale green attribute + peak arbitrage margin
rte_loss_cost_usd_per_mwh | Levelized parasitic charging loss cost | USD/MWh | 35 | Average off-peak wholesale charging cost applied to round-trip losses
federal_clean_energy_grant_offset_pct | IRA Section 48 ITC and federal infrastructure co-funding | Fraction | 0.7 | Reflected directly in net annualized capex figures
carrying_charge_rate | Fixed capital recovery factor & municipal utility discount rate | Fraction | 0.04 | Net annualized capital asset amortization rate
max_grid_headroom_absorption_factor | Transmission substation maximum annual curtailment capture ratio | Fraction | 0.762 | Maximum portion of regional curtailed renewable MWh deliverable through substation tie